## Sheet1
(FILTER PLANT SAVIN) IO LIST SYSTEM CONFIG PARAMETER SETTING

## IO_LIST
IO LIST
INPUT |  |  | SLOT
AC_CONTROL | %I0.0 | 0 | 1
DRV_FAULT1 | %I0.1 | 1
FDBK_MAIN_FAN1 | %I0.2 | 2
FDBK_FIBER_FAN1.1 | %I0.3 | 3
FDBK_FILTER_DISK1 | %I0.4 | 4
FDBK_ROTARY1 | %I0.5 | 5
FDBK_JAROOB1 | %I0.6 | 6
FDBK_DUST_FAN1 | %I0.7 | 7
FDBK_COMP1.1 | %I1.0 | 8
FDBK_COMP1.2 | %I1.1 | 9
FAULT_FIBER_FAN1.1 | %I1.2 | 10
FAULT_FILTER_DISK1 | %I1.3 | 11
FAULT_DUST_FAN1 | %I1.4 | 12
FAULT_COMP1.1 | %I1.5 | 13
FAULT_COMP1.2 | %I2.0 | 14 | 2
DRV_FAULT2 | %I2.1 | 15
FDBK_MAIN_FAN2 | %I2.2 | 16
FDBK_FIBER_FAN2.1 | %I2.3 | 17
FDBK_FILTER_DISK2 | %I2.4 | 18
FDBK_ROTARY2 | %I2.5 | 19
FDBK_JAROOB2 | %I2.6 | 20
FDBK_DUST_FAN2 | %I2.7 | 21
FDBK_COMP2.1 | %I3.0 | 22 | 3
FDBK_COMP2.2 | %I3.1 | 23
FAULT_FIBER_FAN2.1 | %I3.2 | 24
FAULT_FILTER_DISK2 | %I3.3 | 25
FAULT_DUST_FAN2 | %I3.4 | 26
FAULT_COMP2.1 | %I3.5 | 27
FAULT_COMP2.2 | %I3.6 | 28
EMRGENCY1 | %I3.7 | 29
EMRGENCY2 | %I4.0 | 30
TERMOSTAT | %I4.1 | 31
FIRE_ALARM | %I4.2 | 32
PTC_ALARM_1 | %I4.3 | 33
FAULT_FIBER_FAN1.2 | %I4.4 | 34
FAULT_FIBER_FAN2.2 | %I4.5 | 35
SYSTEM_ALARM | %I4.6 | 36
| %I4.7 | 37
OUTPUT |  |  | SLOT
DRIVE_RUN1 | %Q0.0 | 0 | 1
FIBER_FAN1.1 | %Q0.1 | 1
FILTER_DISK1 | %Q0.2 | 2
ROTARY1 | %Q0.3 | 3
JAROOB1 | %Q0.4 | 4
DUST_FAN1 | %Q0.5 | 5
COMP1.1 | %Q0.6 | 6
COMP1.2 | %Q0.7 | 7
DRIVE_RUN2 | %Q1.0 | 8
FIBER_FAN2.1 | %Q1.1 | 9
FILTER_DISK2 | %Q2.0 | 10 | 3
ROTARY2 | %Q2.1 | 11
JAROOB2 | %Q2.2 | 12
DUST_FAN2 | %Q2.3 | 13
COMP2.1 | %Q2.4 | 14
COMP2.2 | %Q2.5 | 15
FIBER_FAN1.2 | %Q2.6 | 16
FIBER_FAN2.2 | %Q2.7 | 17

## HW CONFIG
SYSTEM CONFIG
SLOT 1 | SLOT 2 | SLOT 3
CPU 1214C AC/DC/Rly | SM 1221 DI8 x 24VDC | SM 1223 DI16/DQ16 x relay

## PARAMETER SET
PARAMETER SETTING
|  |  |  | differential pressure 1 |  | MODE | DIP 1 | DIP 2 | DIP 3 | DIP 4 | DIP 5 | DIP 6
| MODBUS RTU |  |  | ADDRESS | 1 |  | ON | OFF | ON | OFF | ON | OFF
| BAD RATE | 9600 bps |  | differential pressure 2 |  | MODE | DIP 1 | DIP 2 | DIP 3 | DIP 4 | DIP 5 | DIP 6
| START BIT | 1 |  | ADDRESS | 2 |  | ON | OFF | ON | OFF | ON | OFF
| DATA BIT | 8 |  | differential pressure 3 |  | MODE | DIP 1 | DIP 2 | DIP 3 | DIP 4 | DIP 5 | DIP 6
| STOP BIT | 2 |  | ADDRESS | 3 |  | ON | OFF | ON | OFF | ON | OFF
| PARITY | NONE |  | differential pressure 4 |  | MODE | DIP 1 | DIP 2 | DIP 3 | DIP 4 | DIP 5 | DIP 6
|  |  |  | ADDRESS | 4 |  | ON | OFF | ON | OFF | ON | OFF
|  |  |  | differential pressure 5 |  | MODE | DIP 1 | DIP 2 | DIP 3 | DIP 4 | DIP 5 | DIP 6
|  |  |  | ADDRESS | 5 |  | ON | OFF | ON | OFF | ON | OFF
|  |  |  | differential pressure 6 |  | MODE | DIP 1 | DIP 2 | DIP 3 | DIP 4 | DIP 5 | DIP 6
|  |  |  | ADDRESS | 6 |  | ON | OFF | ON | OFF | ON | OFF
|  |  |  | differential pressure 7 |  | MODE | DIP 1 | DIP 2 | DIP 3 | DIP 4 | DIP 5 | DIP 6
|  |  |  | ADDRESS | 7 |  | ON | OFF | ON | OFF | ON | OFF
|  |  |  | differential pressure 8 |  | MODE | DIP 1 | DIP 2 | DIP 3 | DIP 4 | DIP 5 | DIP 6
|  |  |  | ADDRESS | 8 |  | ON | OFF | ON | OFF | ON | OFF
| SANTERNO SINUS VEGA PARAMETER 75KW |  |  |  | EMOTRON FDU PARAMETER 90KW |  |  |  | SYSTEM CONFIG
| F0-00 | Command source selection | 1 |  | 213 | Drive Mode | 2
| F0-02 | Main frequency source X selection | 2 |  | 214 | Reference control | 0 |  | SLOT 1 | SLOT 2 | SLOT 3
| F0-05 | Frequency source selection | 0 |  | 215 | Run/Stop Control | 0 |  | CPU 1214C AC/DC/Rly | SM 1221 DI8 x 24VDC | SM 1223 DI16/DQ16 x relay
| F0-12 | Acceleration time 1 | 15S |  | 216 | Reset Control | 5
| F0-13 | Deceleration time 1 | 2S |  | 33B | Stop Mode | 1
| F2-04 | Startup DC braking time | 3S |  | 33C | Brake Release Time | 3S
| F2-08 | Stop mode | 1 |  | 331 | Acceleration Time | 15S
[5 empty] | 332 | Deceleration Time | 2S