## IO_LIST
INPUT |  |  | SLOT
AC_CONTROL | %I0.0 | 0 | 1
DRV_FAULT | %I0.1 | 1
BYPASS_SUPPLY_1 | %I0.2 | 2
BYPASS_SUPPLY_2 | %I0.3 | 3
BYPASS_SUPPLY_3 | %I0.4 | 4
BYPASS_RETURN_1 | %I0.5 | 5
BYPASS_RETURN_2 | %I0.6 | 6
BYPASS_RETURN_3 | %I0.7 | 7
FDBK_PUMP_RUN | %I1.0 | 8
FDBK_DUST_FAN_1 | %I1.1 | 9
FDBK_DUST_FAN_2 | %I1.2 | 10
FDBK_DUST_FAN_3 | %I1.3 | 11
FDBK_DUST_FAN_4 | %I1.4 | 12
FDBK_ROTARY_1 | %I1.5 | 13
FDBK_JAROOB_1 | %I2.0 | 14 | 2
FDBK_ROTARY_2 | %I2.1 | 15
FDBK_JAROOB_2 | %I2.2 | 16
FAULT_FAN_SUPPLY_1 | %I2.3 | 17
FAULT_FAN_SUPPLY_2 | %I2.4 | 18
FAULT_FAN_SUPPLY_3 | %I2.5 | 19
FAULT_FAN_RETURN_1 | %I2.6 | 20
FAULT_FAN_RETURN_2 | %I2.7 | 21
FAULT_FAN_RETURN_3 | %I3.0 | 22 | 3
FIRE_ALARM | %I3.1 | 23
FAULT_DUST_FAN_1 | %I3.2 | 24
FAULT_DUST_FAN_2 | %I3.3 | 25
FAULT_DUST_FAN_3 | %I3.4 | 26
FAULT_DUST_FAN_4 | %I3.5 | 27
FAULT_ROTARY_1 | %I3.6 | 28
FAULT_JAROOB_1 | %I3.7 | 29
FAULT_ROTARY_2 | %I4.0 | 30
FAULT_JAROOB_2 | %I4.1 | 31
FDBK_POWER_DAMPER | %I4.2 | 32
TERMOSTAT | %I4.3 | 33
DOOR1 | %I4.4 | 34
DOOR2 | %I4.5 | 35
FDBK_FAN_EXH | %I4.6 | 36
FAULT_FAN_EXH | %I4.7 | 37
OUTPUT |  |  | SLOT
FAN_SUPPLY_1_k1 | %Q0.0 | 0 | 1
FAN_SUPPLY_1_kB1 | %Q0.1 | 1
FAN_SUPPLY_2_k2 | %Q0.2 | 2
FAN_SUPPLY_2_kB2 | %Q0.3 | 3
FAN_SUPPLY_3_K3 | %Q0.4 | 4
FAN_SUPPLY_3_KB3 | %Q0.5 | 5
FAN_RETURN_1_K4 | %Q0.6 | 6
FAN_RETURN_1_KB4 | %Q0.7 | 7
FAN_RETURN_2_K5 | %Q1.0 | 8
FAN_RETURN_2_KB5 | %Q1.1 | 9
FAN_RETURN_3_K6 | %Q2.0 | 10 | 3
FAN_RETURN_3_KB6 | %Q2.1 | 11
DRIVE_RUN | %Q2.2 | 12
PUMP_RUN | %Q2.3 | 13
DUST_FAN_1 | %Q2.4 | 14
DUST_FAN_2 | %Q2.5 | 15
DUST_FAN_3 | %Q2.6 | 16
DUST_FAN_4 | %Q2.7 | 17
ROTARY1 | %Q3.0 | 18
JAROOB1 | %Q3.1 | 19
ROTARY2 | %Q3.2 | 20
JAROOB2 | %Q3.3 | 21
POWER_DAMPER | %Q3.4 | 22
STEAM_VALVE_POWER | %Q3.5 | 23
FAN_EXH_RUN | %Q3.6 | 24

## HW CONFIG
SLOT 1 | SLOT 2 | SLOT 3 | SLOT 4 | SLOT 5
CPU 1214C AC/DC/Rly | SM 1221 DI8 x 24VDC | SM 1223 DI16/DQ16 x relay | SM 1232 AQ2 | SM 1232 AQ2
|  |  | CH 0 :STEAM VALVE | CH 0 :MACHINE DAMPER
CH 1 :FRESH DAMPER

## PARAMETER SET
|  |  | TEMP & HUMID INDOOR 1 |  | MODE | DIP 1 | DIP 2 | DIP 3 | DIP 4 | DIP 5 | DIP 6
MODBUS RTU |  |  | ADDRESS | 1 |  | ON | OFF | ON | OFF | ON | OFF
BAD RATE | 9600 bps |  | TEMP & HUMID OUTDOOR |  | MODE | DIP 1 | DIP 2 | DIP 3 | DIP 4 | DIP 5 | DIP 6
START BIT | 1 |  | ADDRESS | 2 |  | ON | OFF | ON | OFF | ON | OFF
DATA BIT | 8
STOP BIT | 2
PARITY | NONE
SANTERNO SINUS VEGA PARAMETER 30KW
F0-00 | Command source selection | 1 |  | SLOT 1 | SLOT 2 | DIP 1: SLOT 3; DIP 2: SLOT 4; DIP 4: SLOT 5
F0-02 | Main frequency source X selection | 9 |  | CPU 1214C AC/DC/Rly | SM 1221 DI8 x 24VDC | DIP 1: SM 1223 DI16/DQ16 x relay; DIP 2: SM 1232 AQ2; DIP 4: SM 1232 AQ2
F0-05 | Frequency source selection | 0 |  |  |  | DIP 2: CH 0 :STEAM VALVE; DIP 4: CH 0 :MACHINE DAMPER
F0-12 | Acceleration time 1 | 15S |  |  |  | DIP 2: CH 1 :FRESH DAMPER
F0-13 | Deceleration time 1 | 2S | bar: DIP 1 to DIP 5
F2-04 | Startup DC braking time | 3S | bar: DIP 1 to DIP 5
F2-08 | Stop mode | 0 OR 1
FB-00 | Baud rate | 5
FB-01 | Local address | 3
FB-04 | MODBUS Data format | 3