## Sheet1
(RAZI 1) IO LIST SYSTEM CONFIG PARAMETER SETTING

## IO_LIST
AC-1 INPUT |  |  | SLOT
AC_CONTROL | %I0.0 | 0 | 1
DRV_FAULT | %I0.1 | 1
BYPASS_SUPPLY | %I0.2 | 2
BYPASS_RETURN | %I0.3 | 3
FDBK_PUMP_RUN | %I0.4 | 4
FDBK_ROT-JRB-DU | %I0.5 | 5
FAULT_FAN_SUPPLY | %I0.6 | 6
FAULT_FAN_RETURN | %I0.7 | 7
FDBK_POWER_DAMPER | %I1.0 | 8
TERMOSTAT | %I1.1 | 9
FIRE_ALARM | %I1.2 | 10
DOOR1 | %I1.3 | 11
DOOR2 | %I1.4 | 12
| %I1.5 | 13
| %I2.0 | 14 | 2
| %I2.1 | 15
| %I2.2 | 16
| %I2.3 | 17
| %I2.4 | 18
| %I2.5 | 19
| %I2.6 | 20
| %I2.7 | 21
OUTPUT |  |  | SLOT
FAN_SUPPLY | %Q0.0 | 0 | 1
FAN_RETURN | %Q0.1 | 1
DRIVE_RUN | %Q0.2 | 2
ROT-JRB-DU | %Q0.3 | 3
POWER_DAMPER | %Q0.4 | 4
STEAM_VALVE_POWER | %Q0.5 | 5
| %Q0.6 | 6
| %Q0.7 | 7
| %Q1.0 | 8
S_VALVE | %Q1.1 | 9

## HW CONFIG
SLOT 1 | SLOT 2 | SLOT 3
CPU 1214C AC/DC/Rly | SM 1221 DI8 x 24VDC | SM 1232 AQ2
CH 0 :STEAM VALVE
CH 1 :FRESH DAMPER

## PARAMETER SET
|  |  | TEMP & HUMID INDOOR 1 |  | MODE | DIP 1 | DIP 2 | DIP 3 | DIP 4 | DIP 5 | DIP 6
MODBUS RTU |  |  | ADDRESS | 1 |  | ON | OFF | ON | OFF | ON | OFF
BAUD RATE | 9600 bps |  | TEMP & HUMID OUTDOOR |  | MODE | DIP 1 | DIP 2 | DIP 3 | DIP 4 | DIP 5 | DIP 6
START BIT | 1 |  | ADDRESS | 2 |  | ON | OFF | ON | OFF | ON | OFF
DATA BIT | 8
STOP BIT | 2
PARITY | NONE
LS H100 PARAMETER
DRV-06 | Command source | 1
DRV-07 | Frequency reference source | 6
DRV-03 | Acceleration time | 15 S
DRV-04 | Deceleration time | 2 S
ADV-12 | DC braking time at startup | 3S
ADV-08 | Stop Mode | 0 OR 1
COM-01 | communication inverter ID | 3
COM-02 | Built-in communication protocol | 0
COM-03 | Built-in communication speed | 3
COM-04 | Built-in communication frame setting | 1
Command frequency ADDRESS IS (0h0005) 5-1=4-------->PLC ADDRESS =40005 RANGE (0-5000)