## Sheet1
(RAZI 3) IO LIST SYSTEM CONFIG PARAMETER SETTING

## IO_LIST
AC-3 INPUT |  |  | SLOT
AC_CONTROL | %I0.0 | 0 | 1
DRV_FAULT | %I0.1 | 1
BYPASS_SUPPLY1 | %I0.2 | 2
BYPASS_SUPPLY2 | %I0.3 | 3
BYPASS_SUPPLY3 | %I0.4 | 4
BYPASS_RETURN1 | %I0.5 | 5
BYPASS_RETURN2 | %I0.6 | 6
FDBK_PUMP_RUN | %I0.7 | 7
FDBK_ROT-JRB-DU | %I1.0 | 8
FAULT_FAN_SUPPLY1 | %I1.1 | 9
FAULT_FAN_SUPPLY2 | %I1.2 | 10
FAULT_FAN_SUPPLY3 | %I1.3 | 11
FAULT_FAN_RETURN1 | %I1.4 | 12
FAULT_FAN_RETURN2 | %I1.5 | 13
FDBK_POWER_DAMPER | %I2.0 | 14 | 2
TERMOSTAT | %I2.1 | 15
FIRE_ALARM | %I2.2 | 16
DOOR1 | %I2.3 | 17
DOOR2 | %I2.4 | 18
| %I2.5 | 19
| %I2.6 | 20
| %I2.7 | 21
| %I3.0 | 22
| %I3.1 | 23
| %I3.2 | 24
| %I3.3 | 25
| %I3.4 | 26
| %I3.5 | 27
| %I3.6 | 28
| %I3.7 | 29
OUTPUT |  |  | SLOT
FAN_SUPPLY1 | %Q0.0 | 0 | 1
FAN_SUPPLY2 | %Q0.1 | 1
FAN_SUPPLY3 | %Q0.2 | 2
FAN_RETURN1 | %Q0.3 | 3
FAN_RETURN2 | %Q0.4 | 4
DRIVE_RUN | %Q0.5 | 5
ROT-JRB-DU | %Q0.6 | 6
POWER_DAMPER | %Q0.7 | 7
STEAM_VALVE_POWER | %Q1.0 | 8
S_VALVE | %Q1.1 | 9

## HW CONFIG
SLOT 1 | SLOT 2 | SLOT 3
CPU 1214C AC/DC/Rly | SM 1221 DI16 x 24VDC | SM 1232 AQ2
CH 0 :STEAM VALVE
CH 1 :FRESH DAMPER

## PARAMETER SET
|  |  | TEMP & HUMID INDOOR 1 |  | MODE | DIP 1 | DIP 2 | DIP 3 | DIP 4 | DIP 5 | DIP 6
MODBUS RTU |  |  | ADDRESS | 1 |  | ON | OFF | ON | OFF | ON | OFF
BAUD RATE | 9600 bps |  | TEMP & HUMID OUTDOOR |  | MODE | DIP 1 | DIP 2 | DIP 3 | DIP 4 | DIP 5 | DIP 6
START BIT | 1 |  | ADDRESS | 2 |  | ON | OFF | ON | OFF | ON | OFF
DATA BIT | 8
STOP BIT | 2
PARITY | NONE
LS H100 PARAMETER
DRV-06 | Command source | 1
DRV-07 | Frequency reference source | 6
DRV-03 | Acceleration time | 15 S
DRV-04 | Deceleration time | 2S
ADV-12 | DC braking time at startup | 3S
ADV-08 | Stop Mode | 0 OR 1
COM-01 | communication inverter ID | 3
COM-02 | Built-in communication protocol | 0
COM-03 | Built-in communication speed | 3
COM-04 | Built-in communication frame setting | 1
Command frequency ADDRESS IS (0h0005) 5-1=4-------->PLC ADDRESS =40005 RANGE (0-5000)