## Sheet1
(RAZI 5) IO LIST SYSTEM CONFIG PARAMETER SETTING

## IO_LIST
AC-5 INPUT |  |  | SLOT
AC_CONTROL | %I0.0 | 0 | 1
DRV_FAULT | %I0.1 | 1
BYPASS_SUPPLY1 | %I0.2 | 2
BYPASS_RETURN1 | %I0.3 | 3
BYPASS_RETURN2 | %I0.4 | 4
FDBK_PUMP_RUN | %I0.5 | 5
FDBK_ROT-JRB-DU | %I0.6 | 6
FAULT_FAN_SUPPLY1 | %I0.7 | 7
FAULT_FAN_RETURN1 | %I1.0 | 8
FAULT_FAN_RETURN2 | %I1.1 | 9
FDBK_POWER_DAMPER | %I1.2 | 10
TERMOSTAT | %I1.3 | 11
FIRE_ALARM | %I1.4 | 12
DOOR1 | %I1.5 | 13
DOOR2 | %I2.0 | 14 | 2
| %I2.1 | 15
| %I2.2 | 16
| %I2.3 | 17
| %I2.4 | 18
| %I2.5 | 19
| %I2.6 | 20
| %I2.7 | 21
OUTPUT |  |  | SLOT
FAN_SUPPLY1 | %Q0.0 | 0 | 1
FAN_RETURN1 | %Q0.1 | 1
FAN_RETURN2 | %Q0.2 | 2
DRIVE_RUN | %Q0.3 | 3
ROT-JRB-DU | %Q0.4 | 4
POWER_DAMPER | %Q0.5 | 5
STEAM_VALVE_POWER | %Q0.6 | 6
| %Q0.7 | 7
| %Q1.0 | 8
| %Q1.1 | 9

## HW CONFIG
SLOT 1 | SLOT 2 | SLOT 3
CPU 1214C AC/DC/Rly | SM 1221 DI8 x 24VDC | SM 1232 AQ2
CH 0 :STEAM VALVE
CH 1 :FRESH DAMPER

## PARAMETER SET
|  |  | TEMP & HUMID INDOOR |  | MODE | DIP 1 | DIP 2 | DIP 3 | DIP 4 | DIP 5 | DIP 6
MODBUS RTU |  |  | ADDRESS | 1 |  | ON | OFF | ON | OFF | ON | OFF
BAUD RATE | 9600 bps |  | TEMP & HUMID OUTDOOR |  | MODE | DIP 1 | DIP 2 | DIP 3 | DIP 4 | DIP 5 | DIP 6
START BIT | 1 |  | ADDRESS | 2 |  | ON | OFF | ON | OFF | ON | OFF
DATA BIT | 8
STOP BIT | 2
PARITY | NONE
DANFOSS VLT Automation Drive PARAMETER
1-80 | Function at Stop | 0
1-83 | Precise Stop Function | 0
2-02 | DC Braking Time | 3 S
3-10 | Preset Reference | 0
3-15 | Reference Resource 1 | 11
3-40 | Ramp 1 Type | 2
3-41 | Ramp 1 Ramp Up Time | 15 S
3-42 | Ramp 1 Ramp Down Time | 2 S
8-01 | Control Site | 0
8-02 | Control Word Source | 1
8-30 | Protocol | 2
8-31 | Address | 3
8-32 | FC Port Baud Rate | 2
8-33 | Parity / Stop Bits | 3
8-50 | Coasting Select | 3
8-51 | Quick Stop Select | 3
8-52 | DC Brake Select | 3
8-53 | Start Select | 3
8-56 | Preset Reference Select
Command frequency ADDRESS IS (50010) 50010-1=50009-------->PLC ADDRESS =450010 RANGE (0-16384)