## Sheet1
(RAZI 6) IO LIST SYSTEM CONFIG PARAMETER SETTING

## IO_LIST
AC-6 INPUT |  |  | SLOT
AC_CONTROL | %I0.0 | 0 | 1
DRV_FAULT1 | %I0.1 | 1
DRV_FAULT2 | %I0.2 | 2
BYPASS_SUPPLY1 | %I0.3 | 3
BYPASS_SUPPLY2 | %I0.4 | 4
BYPASS_SUPPLY3 | %I0.5 | 5
BYPASS_RETURN1 | %I0.6 | 6
BYPASS_RETURN2 | %I0.7 | 7
FDBK_PUMP_RUN1 | %I1.0 | 8
FDBK_PUMP_RUN2 | %I1.1 | 9
FDBK_ROT-JRB-DU | %I1.2 | 10
FAULT_FAN_SUPPLY1 | %I1.3 | 11
FAULT_FAN_SUPPLY2 | %I1.4 | 12
FAULT_FAN_SUPPLY3 | %I1.5 | 13
FAULT_FAN_RETURN1 | %I2.0 | 14 | 2
FAULT_FAN_RETURN2 | %I2.1 | 15
FDBK_POWER_DAMPER | %I2.2 | 16
TERMOSTAT | %I2.3 | 17
FIRE_ALARM | %I2.4 | 18
DOOR1 | %I2.5 | 19
DOOR2 | %I2.6 | 20
| %I2.7 | 21
OUTPUT |  |  | SLOT
FAN_SUPPLY1 | %Q0.0 | 0 | 1
FAN_SUPPLY2 | %Q0.1 | 1
FAN_SUPPLY3 | %Q0.2 | 2
FAN_RETURN1 | %Q0.3 | 3
FAN_RETURN2 | %Q0.4 | 4
DRIVE_RUN1 | %Q0.5 | 5
DRIVE_RUN2 | %Q0.6 | 6
ROT-JRB-DU | %Q0.7 | 7
POWER_DAMPER | %Q1.0 | 8
STEAM_VALVE_POWER | %Q1.1 | 9
| %Q2.0 | 10 | 2
| %Q2.1 | 11
| %Q2.2 | 12
| %Q2.3 | 13
| %Q2.4 | 14
| %Q2.5 | 15
| %Q2.6 | 16
| %Q2.7 | 17

## HW CONFIG
SLOT 1 | SLOT 2 | SLOT 3
CPU 1214C AC/DC/Rly | SM 1223 DI8/DQ8 x 24VDC | SM 1232 AQ2
CH 0 :STEAM VALVE
CH 1 :FRESH DAMPER

## PARAMETER SET
|  |  | TEMP & HUMID INDOOR 1 |  | MODE | DIP 1 | DIP 2 | DIP 3 | DIP 4 | DIP 5 | DIP 6
MODBUS RTU |  |  | ADDRESS | 1 |  | ON | OFF | ON | OFF | ON | OFF
BAUD RATE | 9600 bps |  | TEMP & HUMID OUTDOOR |  | MODE | DIP 1 | DIP 2 | DIP 3 | DIP 4 | DIP 5 | DIP 6
START BIT | 1 |  | ADDRESS | 2 |  | ON | OFF | ON | OFF | ON | OFF
DATA BIT | 8
STOP BIT | 2
PARITY | NONE
DANFOSS VLT Automation Drive PARAMETER |  |  |  | DANFOSS VLT Automation Drive PARAMETER
1-80 | Function at Stop | 0 |  | 1-80 | Function at Stop | DIP 1: 0
1-83 | Precise Stop Function | 0 |  | 1-83 | Precise Stop Function | DIP 1: 0
2-02 | DC Braking Time | 3 S |  | 2-02 | DC Braking Time | DIP 1: 3 S
3-10 | Preset Reference | 0 |  | 3-10 | Preset Reference | DIP 1: 0
3-15 | Reference Resource 1 | 11 |  | 3-15 | Reference Resource 1 | DIP 1: 11
3-40 | Ramp 1 Type | 2 |  | 3-40 | Ramp 1 Type | DIP 1: 2
3-41 | Ramp 1 Ramp Up Time | 15 S |  | 3-41 | Ramp 1 Ramp Up Time | DIP 1: 15 S
3-42 | Ramp 1 Ramp Down Time | 2 S |  | 3-42 | Ramp 1 Ramp Down Time | DIP 1: 2 S
8-01 | Control Site | 0 |  | 8-01 | Control Site | DIP 1: 0
8-02 | Control Word Source | 1 |  | 8-02 | Control Word Source | bar: DIP 1
8-30 | Protocol | 2 |  | 8-30 | Protocol | DIP 1: 2
8-31 | Address | 3 |  | 8-31 | Address | DIP 1: 4
8-32 | FC Port Baud Rate | 2 |  | 8-32 | FC Port Baud Rate | DIP 1: 2
8-33 | Parity / Stop Bits | 3 |  | 8-33 | Parity / Stop Bits | DIP 1: 3
8-50 | Coasting Select | 3 |  | 8-50 | Coasting Select | DIP 1: 3
8-51 | Quick Stop Select | 3 |  | 8-51 | Quick Stop Select | DIP 1: 3
8-52 | DC Brake Select | 3 |  | 8-52 | DC Brake Select | DIP 1: 3
8-53 | Start Select | 3 |  | 8-53 | Start Select | DIP 1: 3
8-56 | Preset Reference Select |  |  | 8-56 | Preset Reference Select
Command frequency ADDRESS IS (50010) 50010-1=50009-------->PLC ADDRESS =450010 RANGE (0-16384) |  |  |  | Command frequency ADDRESS IS (50010) 50010-1=50009-------->PLC ADDRESS =450010 RANGE (0-16384)