## Sheet1
(SIMABAFT) (4) IO LIST SYSTEM CONFIG PARAMETER SETTING

## IO_LIST
INPUT |  | SLOT
AC_CONTROL | 0 | 1
FDBK_SUPPLY_1 | 1
FDBK_SUPPLY_2 | 2
FDBK_RETURN_1 | 3
FDBK_RETURN_2 | 4
FDBK_RETURN_3 | 5
FDBK_PUMP_RUN | 6
FDBK_DUST_FAN_1 | 7
FDBK_DUST_FAN_2 | 8
FDBK_DUST_FAN_3 | 9
FDBK_DUST_FAN_4 | 10
FDBK_ROTARY_1 | 11
FDBK_ROTARY_2 | 12
FDBK_JAROOB_1 | 13
FDBK_JAROOB_2 | 14 | 2
FDBK_POWER_DAMPER | 15
FAULT_DRIVE | 16
FAULT_DRIVE_MPCB | 17
FAULT_FAN_SUPPLY_1 | 18
FAULT_FAN_SUPPLY_2 | 19
FAULT_FAN_RETURN_1 | 20
FAULT_FAN_RETURN_2 | 21
FAULT_FAN_RETURN_3 | 22 | 3
FAULT_DUST_FAN_1 | 23
FAULT_DUST_FAN_2 | 24
FAULT_DUST_FAN_3 | 25
FAULT_DUST_FAN_4 | 26
FAULT_ROTARY_1 | 27
FAULT_ROTARY_2 | 28
FAULT_JAROOB_1 | 29
FAULT_JAROOB_2 | 30 | 4
TERMOSTAT_ALARM | 31
FIRE_ALARM | 32
DOOR1 | 33
DOOR2 | 34
35
36
37
OUTPUT |  | SLOT
FAN_SUPPLY_1_k1 | 0 | 1
FAN_SUPPLY_1_kB1 | 1
FAN_SUPPLY_2_K2 | 2
FAN_SUPPLY_2_kB2 | 3
FAN_RETURN_1_K3 | 4
FAN_RETURN_1_Kb3 | 5
FAN_RETURN_2_K4 | 6
FAN_RETURN_2_kB4 | 7
FAN_RETURN_3_K5 | 8
FAN_RETURN_3_Kb5 | 9
DRIVE_RUN | 10 | 2
PUMP_RUN | 11
DUST_FAN_1 | 12
DUST_FAN_2 | 13
DUST_FAN_3 | 14
DUST_FAN_4 | 15
ROTARY1 | 16
JAROOB1 | 17
ROTARY2 | 18 | 3
JAROOB2 | 19
DAMPER_POWER | 20
STEAM_VALVE_POWER | 21
22
23
24
25

## HW CONFIG
SLOT 1 | SLOT 2 | SLOT 3 | SLOT 4 | SLOT 5 | SLOT 6
CPU 1215C AC/DC/Rly | SM 1223 DI8/DQ8x relay | SM 1223 DI8/DQ8x relay | SM 1221 DI8x 24VDC | SM 1231 AI4 | SM 1232 AQ4
|  |  |  | CH 0 :TEMP IN | CH 0 :FREQ REF
|  |  |  | CH 1 :HUMID IN | CH 1 :FRESH DAMPER
|  |  |  | CH 2 :TEMP OUT | CH 2 :STEAM VALVE
|  |  |  | CH 3 :HUMID OUT | CH 3 :

## PARAMETER SET
LS H100 PARAMETER
DRV-06 | Command source | 1
DRV-07 | Frequency reference source | 2
DRV-03 | Acceleration time | 15 S
DRV-04 | Deceleration time | 2 S
ADV-07 | Start Mode | 1
ADV-08 | Stop Mode | 1
ADV-12 | DC braking time at startup | 3S
OUT-32 | RELAY 2 | 14